- SECTION 12 35 56 - Free Standing Laboratory Workstation System

- PART 1: DESCRIPTION OF WORK

- 1.00	SUMMARY AND SCOPE

- Section Includes:

- Tables

- Support Frames and Structures

- Shelves

- Work Surfaces

- Post mounted gas fixtures

- Suspended cabinets

- Mobile cabinets

- Service lines and connections

- Ceiling manifold system

- Pre-plumbing and pre-wiring is required for Free Standing Workstations where called for in these specifications, equipment schedules or shown on drawings. When pre-plumbed, plumbing service piping shall terminate at a single point connection at the top of the vertical support frame as specified or as shown on drawings. Pre-wired power service shall terminate with a power cord pig tail at the top of the support frame or below the work surface frame as specified, or as shown on drawings.

- Utility service outlet accessory fittings, electrical receptacles, and switches, as listed in these specifications, equipment schedules or as shown on drawings as mounted on the laboratory furniture, not specified as pre-plumbed or pre-wired, shall be furnished only. The above-defined items shall be furnished with supply tank nipples and lock nuts, loose in boxes and properly marked. These plumbing and electrical fittings will be packaged separately and properly marked for delivery to the appropriate contractor.

- Furnishing and delivering, packed in boxes for installation by the mechanical contractor, all laboratory sinks, cup sinks or drains, drain troughs, overflows and sink outlets with integral tailpieces, which occur above the floor, and where these items are part of the equipment or listed in the specifications, equipment schedules or shown on the drawings. Integral tailpieces when required shall be in accordance with the manufacturer's standards. All tailpieces shall be furnished less the couplings required to connect them to the drain piping system.

- Furnishing service strip supports where specified, and setting in place service tunnels, service turrets, supporting structures and reagent racks of the type shown on the details.

- Removal of all debris, dirt and rubbish accumulated as a result of the installation of the laboratory furniture to an onsite container provided by others, leaving the premises clean and orderly.

- Related Divisions:

- Divisions 5 & 6:	In-Wall Blocking and Studs

- Division 11:		Chemical Fume Hoods

- Division 12:		Laboratory Casework

- Division 15:		Plumbing Division

- Division 16:		Electrical Fittings and Connections

- Related Publications:

- SEFA 10 – Scientific Equipment and Furniture Association

- NFPA 30 – National Fire Protection Association

- NFPA-45 – National Fire Protection Association

- UL – Underwriters Laboratories. If required, the manufacturer shall provide UL certification for the lab benches.  Upon delivery, the manufacturer must provide a letter from Underwriters Laboratories specifically referencing the project and certifying that the benches have been inspected and marked with a UL sticker indicating compliance.

- ASTM D522 – Bending Test

  - BASIS OF WORK

- It is the intent of this specification to use Enterprise System by Kewaunee Scientific Corporation as the standard of construction for laboratory furniture. The construction standards of this product line shall provide the basis for quality and function.

- Supply all equipment in accordance with this specification. The offering of a product differing in materials and construction from this specification requires written approval from the owner/architect. This approval must be obtained fourteen (14) days before the quotation deadline. Procedures for obtaining approval for an alternate manufacturer are defined in section 2.00.C in this specification.

- General Contractors should secure a list of approved laboratory furniture manufacturers from the architect as a protection against non-conformance to these specifications.

- Participants in the quotation process have the option of clarifying deviations to the specified design, construction, or materials. Without such clarifications, sealed quotations to the owner or owner representative will be construed as being in total conformance to the requirements of the specification.

- The owner / owner representative reserves the right to reject qualified or alternate proposals and to award based on product value where such action assures the owner greater integrity of product.

- 1.02	QUALITY ASSURANCE

- The modular component system laboratory furniture contractor shall also provide work tops and fume hoods all manufactured or shipped from the same geographic location to assure proper quality, staging, shipment and single source responsibility.

- General Performance: Provide certification that furniture shall meet the performance requirements described in SEFA 8 and SEFA 10.

- General Performance:  Provide certification that furniture shall meet the load rating criteria described in 2.02:  2,800# for Double Frame Workstations, 1,400# for Single Frame Workstations.

- The free standing workstation system contractor shall also provide laboratory furniture, work tops, and fume hoods all manufactured or shipped from the same geographic location to assure proper staging, shipment and single source responsibility.

- All material should be manufactured in the United States at a modern plant with proper tools, dies, fixtures and skilled productions staff.  Provide location of domestic, United States facilities used for this project.

- Finish Performance: Provide independent test lab certification that the furniture finish shall meet the performance requirements described in section 2.03 of these specifications.

- The Dealer for the qualified manufacturer (if applicable) must have been in the laboratory casework business for at least ten (10) years.

- Provide storage for laboratory workstations, suspended and mobile casework , shelving, and countertops for just-in-time delivery and stocking on the jobsite at no charge to the Owner or General Contractor.

- Provide a project specific quality control program for this project to include bench load testing, workstation construction, frame construction, wood cabinetry finish and wood graining, steel cabinet construction, workstation service line pressure testing after delivery to the jobsite, and final jobsite installation.

- SUBMITTALS

- Manufacturer's Data: Submit manufacturer's data and installation instructions for each type of casework. Provide data indicating compliance with SEFA 8 and SEFA 10.

- Samples:
Samples from non-specified manufacturers will be required and reviewed per specification. Samples shall be delivered, at no cost to the architect or owner to a destination set forth by the architect or owner. This must be done fourteen (14) days before quotation deadline as a condition of approval of each bidder. Samples shall be full size, production type samples. Miniature, or "Show Room" type samples are not acceptable. Furnish the following:

- Complete table structure with shelves and accessories, mobile/suspended cabinet and required hardware.

- One sample of all top materials shown or called for of sufficient size to perform finish requirement tests.

- Sample of all mechanical service fittings, locks, door pulls, hinges, and interior hardware.

- Shop Drawings:
Submit shop drawings for furniture assemblies showing plans, elevations, ends, cross-sections, service run spaces, location and type of service fittings.

- Coordinate shop drawings with other work involved.

- Provide roughing-in drawings for mechanical and electrical services when required.

- Provide project specific quality control program as described in 1.02 Quality Assurance.

- PART 2 – PRODUCTS

- 2.00	MANUFACTURERS

- The basis of this specification is laboratory furniture systems manufactured according to the standards used by Kewaunee Scientific Corporation and Nycom, Inc.

- All laboratory equipment covered by the specification shall be the product of one manufacturer and be fabricated at one geographic location in the United States to assure shipping continuity and single-source responsibility.

- Products must be provided from one of the following manufacturers.  Approval below does not approve the manufacturer’s standard product.  Each bidder must fully comply with this specification.  No other bidders will be approved.

- Kewaunee Scientific Corporation, Nycom, Inc.  BASIS OF DESIGN

- Jamestown Metal Projects

- AT Villa, Inc

- The selected manufacturer must warrant for a period of one-year starting (date of acceptance or occupancy, whichever comes first) that all products sold under the contract referenced above shall be free from defects in material and workmanship. Purchaser shall notify the manufacturer’s representative immediately of any defective product. The manufacturer shall have a reasonable opportunity to inspect the goods. The purchaser shall return no product until receipt by purchaser of written shipping instructions from the manufacturer.

- 2.01	MATERIALS

- General Requirements:
It is the intent of this specification to provide a high quality adjustable and moveable casework system designed for the laboratory environment. Major structural components are made from high quality cold rolled steel.

- Steel:
Cold rolled sheet steel shall be prime grade; roller leveled, and shall be treated at the mill to be free of scale, ragged edges, deep scratches or other injurious effects. All gauges shall be U.S. Standard.  No galvanized steel is permitted.

- Glass:   
Glass used for framed sliding and swinging doors shall be 1/8” float glass. Glass used for unframed sliding doors, shall be 1/4” float glass.

- CONSTRUCTION

- A.	Freestanding Workstation system shall be comprised of Work Surface Support Frames adjustable from 30” to 37” AFF, in one inch increments, and a Rear Frame Support Structure, single or double sided, incorporating a vertical post and horizontal support. The vertical supports shall incorporate individual slots for adjustable shelving, hanging wall cases and accessories. The vertical support shall incorporate a chase for plumbing and wiring of services.

- Work Surface Support Frame:

- The frame shall be a welded four sided assembly consisting of 11 gauge steel channel formations, front adjustable height legs, and rear attachment collars. Nominal lengths are 42”, 48”, 60”, 72” and 96”.

- Adjustable height shall be from 30” to 37” AFF (allowing for a 1” work surface).

- Front leg members shall be 11 gauge steel tubes, 2” outside diameter and 1.75” inner telescoping leg capable of vertical adjustment in 1” increments.

- Legs shall include non-marring, 3/8” diameter, levelers with nylon glides.

- Rear corners shall have 2.25” diameter x 6” high, 11 gauge half-round collars welded to the work surface frame with supporting gussets and shall be mechanically fastened to the rear upright supports with Button Head Socket Cap Screws.

- Load rating shall be 100 lbs per linear foot of length to a maximum of 800lbs/frame With uniformly distributed load, the maximum allowable deflection shall be .125” measured at the center of the front rail.

- Work surface frames must be capable of allowing for the attachment of both of the following items.  These accessories must be removable and interchangeable with the use of simple tools and without welding or cutting of welds.

  - 1. A full length horizontal rear cabinet stop shall be located under the work 	 	 surface frame to position 24” deep mobile base cabinets 1” behind the front edge of the work surface.

  - 2. Full length continuous rail and hardware to hang suspended cabinets from the bottom of the work surface support frame.

- Double-sided Rear Frame Support Structure:

- The rear frame support structure shall be 84” in height and available in nominal lengths of 48”, 60”, 72”, and 96”.

- Rear frame support structures shall consist of three (3) vertical members; outside two verticals are full height comprised by two 2” diameter legs held together by horizontal framing members. Middle vertical member is 2”x6” oval shaped and runs in-between the upper and intermediate horizontal members.  Asymmetrical, non-oval vertical frames will not be acceptable.

- The middle vertical members shall be able to accommodate up to three services and wiring for electrical and data requirements on horizontal raceway. Middle vertical members also to accommodate split shelving and wall cases hung with mounting hardware.

- The vertical members shall have shelf/accessory slots punched on 1” increments on the front and back starting at 55” above AFF to top of upright.

- Each full height vertical member shall include two (2) non-marring, 3/8” diameter, levelers with nylon glides.

- Rear frame support structures shall incorporate upper and intermediate horizontal cross rails. The upper cross rail shall provide a utility trough the full length of the table. The intermediate cross rail shall support an integral multi-channel raceway for gas services, data and electrical lines (data separated from electrical).

- Needle valve gas service fixtures shall be provided attached to the frame and pre-piped from the factory with 3/8” diameter PVC lines for non-burning gases or stainless steel lines for burning gases.  Each service is to connect to a dual needle valve fixture mounted to the intermediate rail with one valve accessible from each side of the frame.  Valves shall have replaceable color-coded tabs labeled to indicate the type of service.  For PVC lines, the color of the tab should match the color of service lines connecting the frame to the ceiling service manifold.

- Table frames shall be able to be attached to the rear support frame on both sides.  Systems that require additional legs are not acceptable.

- Single-sided Rear Frame Support Structure:

- The rear frame support structure shall be 84” in height and available in nominal lengths of 42”, 48”, 60”, 72”, and 96”.

- Rear frame support structures shall consist of two (2) 2” diameter tube vertical members, with horizontal framing members. The vertical members shall allow the installation of service fittings.

- The vertical members shall be able to accommodate up to three services each and a duplex electrical receptacle or data outlet.

- Vertical members shall include non-marring, 3/8” diameter, levelers.

- All rear frame support structures in widths of 60” wide and over shall have a center support to accommodate split shelving.  Frames without split shelving are not acceptable.

- The vertical members shall have shelf/accessory slots punched on 1” increments on the front starting at 55” above AFF to top of upright.

- Rear frame support structures shall incorporate upper and intermediate horizontal cross rails. The intermediate cross rail shall support an integral two channel raceway, data separated from electrical, with removable access panel.

- Needle valve gas service fixtures shall be provided attached to the frame and pre-piped from the factory with 1/4” diameter copper supply lines for non-burning gases or stainless steel lines for burning gases.  Each service is to connect to a single needle valve fixture mounted to the post.  The finish on the needle valves is to be chrome.  Valves shall have replaceable color-coded tabs labeled to indicate the type of service.  For copper lines, the color of the tab should match the color of service lines connecting the frame to the ceiling service manifold.

- Enterprise Four Leg Adjustable Table

- a.	 The Enterprise four leg table shall consist of a work surface support frame as described above in A.1. Nominal lengths are 42”, 48”, 60”, 72” and 96”. Two additional leg members shall be bolted to the rear attachment collars to provide a four leg self-supporting table frame., adjustable in height from 30” to 37” AFF (allowing for a 1” work surface)

- Front and rear leg members shall be 11 gauge steel tubes, 2” outside diameter and 1.75” inner telescoping leg capable of vertical adjustment in 1” increments

- Legs shall include non-marring, 3/8” diameter, levelers.

- Load rating shall be 100lbs per linear foot of length to a maximum of 800lbs on each counter and 2800lbs for overall double assembly. With uniformly distributed load, the maximum allowable deflection shall be .125” measured at the front center rail.

- B.   Work Surfaces:  SPECIFIER TO EDIT FOR COUNTERTOP MATERIAL AND STYLE
Counter tops shall be as indicated on the drawings or as indicated by model number, and all clips, screws and parts for fastening top to table frame and/or cabinet shall be included.

- Epoxy Resin:

- Molded epoxy resin tops shall be molded from a modified epoxy resin that has been especially compounded and cured to provide the optimum physical and chemical resistance properties required of a heavy-duty laboratory table top. Tops and curbs shall be a uniform mixture throughout their full thickness, and shall not depend upon a surface coating that is readily removed by chemical and/or physical abuse. Tops and curbs shall be non-glaring, Slate in color. Table tops shall be 1" thick, with drip grooves provided on the underside at all exposed edges.  SPECIFIER TO SELECT RESIN COLOR

- C.	Adjustable Shelving

- Adjustable Shelves for Enterprise tables shall be supported by 11 gauge brackets which mount to the slots in the rear frame support structure. They shall be adjustable in height on 1" increments.

- Shelves shall be available in depths of 9", 12", and 15” and nominal lengths of 30”, 36”, 42” and 48” to match the slots on the rear frame support structure.

- Shelf MaterialsSPECIFIER TO EDIT FOR MATERIAL AND STYLE

- a.	Steel shelves shall be 16 gauge steel, formed down 1" then returned back and up into a channel formation. They shall attach securely to the shell brackets without the use or fasteners or adhesive and shall be installable without tools.  Screws with exposed threads will not be acceptable.

- D.	Casework:  SPECIFIER TO EDIT FOR PROJECT CASEWORK MATERIALS & STYLES
Casework for the Enterprise freestanding laboratory casework system shall include suspended style cabinets in compliance with section 12 35 53.

- 2.03	Finish and Performance Requirements

- Steel Paint System Finish and Performance Specification:

- Steel Paint System Finish:
After the component parts have been completely welded together and before finishing, they shall be given a pre-paint treatment to provide excellent adhesion of the finish system to the steel and to aid in the prevention of corrosion. Physical and chemical cleaning of the steel shall be accomplished by washing with an alkaline cleaner, followed by a spray treatment with a complex metallic phosphate solution to provide a uniform fine grained crystalline phosphate surface that shall provide both an excellent bond for the finish and enhance the protection provided by the finish against humidity and corrosive chemicals. 

After the phosphate treatment, the steel shall be dried and all steel surfaces shall be coated with a chemical and corrosion-resistant, environmentally friendly, electrostatically applied powder coat finish. All components shall be individually painted, insuring that no area be vulnerable to corrosion due to lack of paint coverage. The coating shall then be cured by baking at elevated temperatures to provide maximum properties of corrosion and wear resistance. 

The completed finish system in standard colors shall meet the performance test requirements specified under PERFORMANCE TEST RESULTS.

- Performance Test Results (Chemical Spot Tests):

- Testing Procedure:
Chemical spot tests for non-volatile chemicals shall be made by applying 5 drops of each reagent to the surface to be tested and covering with a 1-1/4" dia. watch glass, convex side down to confine the reagent. Spot tests of volatile chemicals shall be tested by placing a cotton ball saturated with reagent on the surface to be tested and covering with an inverted 2-ounce wide mouth bottle to retard evaporation. All spot tests shall be conducted in such a manner that the test surface is kept wet throughout the entire test period, and at a temperature of 77° ±3° F. For both methods, leave the reagents on the panel for a period of one hour. At the end of the test period, the reagents shall be flushed from the surface with water, and the surface scrubbed with a soft bristle brush under running water, rinsed and dried. Volatile solvent test areas shall be cleaned with a cotton swab soaked in the solvent used on the test area. Immediately prior to evaluation, 16 to 24 hours after the reagents are removed, the test surface shall be scrubbed with a damp paper towel and dried with paper towels.

- Test Evaluation:
Evaluation shall be based on the following rating system.

Level 0	–	No detectable change.
Level 1	–	Slight change in color or gloss.
Level 2	–	Slight surface etching or severe staining.
Level 3	–	Pitting, cratering, swelling, or erosion of coating. Obvious and significant deterioration.

After testing, panel shall show no more than three (3) Level 3 conditions.

- Test Reagents

- Test No.	Chemical Reagent	Test Method

- 1.	Acetate, Amyl	Cotton ball & bottle

- 2.	Acetate, Ethyl	Cotton ball & bottle

- 3.	Acetic Acid, 98%	Watch glass

- 4.	Acetone	Cotton ball & bottle

- 5.	Acid Dichromate, 5%	Watch glass

- 6.	Alcohol, Butyl	Cotton ball & bottle

- 7.	Alcohol, Ethyl	Cotton ball & bottle

- 8.	Alcohol, Methyl	Cotton ball & bottle

- 9.	Ammonium Hydroxide, 28%	Watch glass

- 10.	Benzene	Cotton ball & bottle

- 11.	Carbon Tetrachloride	Cotton ball & bottle

- 12.	Chloroform	Cotton ball & bottle

- 13.	Chromic Acid, 60%	Watch glass

- 14.	Cresol	Cotton ball & bottle

- 15.	Dichlor Acetic Acid	Cotton ball & bottle

- 16.	Dimethylformanide	Cotton ball & bottle

- 17.	Dioxane	Cotton ball & bottle

- 18.	Ethyl Ether	Cotton ball & bottle

- 19.	Formaldehyde, 37%	Cotton ball & bottle

- 20.	Formic Acid, 90%	Watch glass

- 21.	Furfural	Cotton ball & bottle

- 22.	Gasoline	Cotton ball & bottle

- 23.	Hydrochloric Acid, 37%	Watch glass

- 24.	Hydrofluoric Acid, 48%	Watch glass

- 25.	Hydrogen Peroxide, 3%	Watch glass

- 26.	Iodine, Tincture of	Watch glass

- 27.	Methyl Ethyl Ketone	Cotton ball & bottle

- 28.	Methylene Cloride	Cotton ball & bottle

- 29.	Mono Chlorobenzene	Cotton ball & bottle

- 30.	Naphthalene	Cotton ball & bottle

- 31.	Nitric Acid, 20%	Watch glass

- 32.	Nitric Acid, 30%	Watch glass

- 33.	Nitric Acid, 70%	Watch glass

- 34.	Phenol, 90%	Cotton ball & bottle

- 35.	Phosphoric Acid, 85%	Watch glass

- 36.	Silver Nitrate, Saturated	Watch glass

- 37.	Sodium Hydroxide, 10%	Watch glass

- 38.	Sodium Hydroxide, 20%	Watch glass

- 39.	Sodium Hydroxide, 40%	Watch glass

- 40.	Sodium Hydroxide, Flake	Watch glass

- 41.	Sodium Sulfide, Saturated	Watch glass

- 42.	Sulfuric Acid, 33%	Watch glass

- 43.	Sulfuric Acid, 77%	Watch glass

- 44.	Sulfuric Acid, 96%	Watch glass

- 45.	Sulfuric Acid, 77% and

- Nitric Acid, 70%, equal parts	Watch glass

- 46.	Toluene	Cotton ball & bottle

- 47.	Trichloroethylene	Cotton ball & bottle

- 48.	Xylene	Cotton ball & bottle

- 49.	Zinc Chloride, Saturated	Watch glass

- * Where concentrations are indicated, percentages are by weight.

- Performance Test Results (Heat Resistance):
Hot water (190° F - 205° F) shall be allowed to trickle (with a steady stream at a rate not less than 6 ounces per minute) on the finished surface, which shall be set at an angle of 45° from horizontal, for a period of five minutes. After cooling and wiping dry, the finish shall show no visible effect from the hot water treatment.

- Performance Test Results (Impact Resistance):
A one-pound ball (approximately 2" diameter) shall be dropped from a distance of 12 inches onto the finished surface of steel panel supported underneath by a solid surface. There shall be no evidence of cracks or checks in the finish due to impact upon close eye-ball examination.

- Performance Test Results (Bending Test):
An 18 gauge steel strip, finished as specified, when bent 180o over a 1/2" diameter mandrel, shall show no peeling or flaking off of the finish.

- Performance Test Results (Adhesion):
Ninety or more squares of the test sample shall remain coated after the scratch adhesion test. Two sets of eleven parallel lines 1/16" apart shall be cut with a razor blade to intersect at right angle thus forming a grid of 100 squares. The cuts shall be made just deep enough to go through the coating, but not into the substrate. They shall then be brushed lightly with a soft brush. Examine under 100 foot-candles of illumination. Note: This test is based on ASTM D2197-68, "Standard Method of Test for Adhesion of Organic Coatings".

- Performance Test Results (Hardness):
The test sample shall have a hardness of 4-H using the pencil hardness test. Pencils, regardless of their brand are valued in this way: 8-H is the hardest, and next in order of diminishing hardness are 7-H, 6-H, 5-H, 4-H, 3-H, 2-H, F, HB, B (soft), 2-B, 3-B, 4-B, 5-B (which is the softest).

- The pencils shall be sharpened on emery paper to a wide sharp edge. Pencils of increasing hardness shall be pushed across the paint film in a chisel-like manner until one is found that will cut or scratch the film. The pencil used before that one, that is, the hardest pencil that will not rupture the film, is then used to express or designate the hardness.

- 2.04	SERVICE CONNECTIONS

- All final connections of service lines from laboratory bench frames to ceiling manifolds shall be included in the scope of this section.

- Quick connects shall be keyed differently among services to prevent service lines from cross connecting.  Each keyed disconnect shall include nipple and coupler with color-keyed band marking media.

- Electrical pig tails shall be SJ 12/4 cable with NEMA L14-20P plugs, unless otherwise stated on the drawings.

- Data punch outs provided by this specification section.  Cabling, RJ45 Jack, outlet, etc. shall be provided and installed by the Electrical Contractor to meet Owner’s data requirements.

- 2.05	CEILING MANIFOLD SERVICE PANELS

- General requirements: Ceiling utility panel shall be fabricated to rest securely in a typical acoustical ceiling T-grid.

- Electrical receptacles shall be NEMA L14-20R, unless otherwise noted, and must be mounted inside electrical boxes attached to top side of the ceiling panel.  This section will include the junction box, receptacle and cover plates only.

- Data punch-outs as indicated.  Data receptacles are CAT6 RJ45, provided and installed by Electrical Contractor to meet Owner’s data requirements.

- Manifold panels will deliver with 3” deep junction boxes factory attached. Electrical outlets, and cover plates are furnished as part of this specification section.  Data outlets, cabling, cover plates, etc. will be provided and installed by the Electrical Contractor per Owner’s requirements.

- Manifold panels shall be a minimum of 18-gauge cold rolled steel with a urethane powder coat finish meeting the requirements of section 2.03 of this specification.

- Ceiling manifold panel system shall be equipped with female quick disconnect bulkhead fitting for non-burning and burning gas services. Each keyed disconnect shall include nipple and coupler with color-keyed band marking media.

- PART 3 - EXECUTION - LABORATORY CASEWORK AND RELATED PRODUCTS

- 3.00	SITE EXAMINATION

- The owner and/or his representative shall assure all building conditions conducive to the installation of a finished goods product; all critical dimensions and conditions previously checked have been adhered to by other contractors (general, mechanical, electrical, etc.) to assure a quality installation.

- Attend meetings on-site to help the owner and/or his representative prepare and coordinate the casework delivery and sequenced installation.

- 3.01	INSTALLATION

- Preparation:
Prior to beginning installation of casework, check and verify that no irregularities exist that would affect quality of execution of work specified.

- Coordination:

- 1.  	Coordinate the work of the Section with the schedule and other requirements of other work being prepared in the area at the same time both with regard to mechanical and electrical connections to and in the fume hoods and the general construction work.

- Participate in on-going, on-site coordination meetings with general contractor, Architect, and owner.

- Storage:

- Provide storage for laboratory workstations, suspended and mobile casework, shelving, and countertops for phased just-in-time delivery and stocking on the jobsite at no charge to the Owner or General Contractor.

- Performance:

- Casework:

- Set casework components plumb, square, and straight with no distortion and securely anchor to building structure. Shim as required using concealed shims.

- Bolt continuous cabinets together with joints flush, tight and uniform, and with alignment of adjacent units within 1/16" tolerance.

- Secure wall cabinets to solid supporting material, not to plaster, lath or gypsum board.

- Abut top edge surfaces in one true plane. Provide flush joints not to exceed 1/8" between top units.

- Pressurize and test all Free Standing Laboratory Workstation plumbing lines for period of 24hrs to confirm absence of leaks prior to connecting to overhead ceiling service panel bulkhead fittings.

- Work surfaces:

- Where required due to field conditions, scribe to abutting surfaces.

- Only factory prepared field joints, located per approved shop drawings, shall be permitted. Secure the joints in the field, where practical, in the same manner as in the factory.

- Secure work surfaces to casework and equipment components with materials and procedures recommended by the manufacturer.

- Adjust and Clean:

- Repair or remove and replace defective work, as directed by owner and/or his representative upon completion of installation.

- Adjust doors, drawers and other moving or operating parts to function smoothly.

- Clean shop finished casework; touch up as required.

- Clean work surfaces and leave them free of all grease and streaks.

- Casework to be left broom clean and orderly.

- Protection:

- Provide reasonable protective measures to prevent casework and equipment from being exposed to other construction activity including 6mil self adhesive film imprinted with warning labels in both English and Spanish.

- Advise owner and/or his representative of procedures and precautions for protection of material, installed laboratory casework and fixtures from damage by work of other trades.